Residential Cross Connection Survey

This survey is being performed in accordance with; WI DNR 810.15,  Chapter-Comm. 81, 82, 84  and the Local  Municipal Ordinance for Cross Connection Control  to ensure safe drinking water.

Compliant? Yes(no further action required          Non-Compliant See table below for corrective action



Name____________________________________________________________________________________

Address_______________________________________ City________________________________________

Phone_________________________________________ Date of Survey _____________________________

Brochure provided in lieu of surveying normal kitchen and bathroom fixtures? Yes

| Fixture Type | Approved | Location / Description | *Device |
| --- | --- | --- | --- |
| Water Softener Drain | Y / N |  | ASME A112.1.2 Vacuum breaker tee, ASME a112.1.3 |
| Laundry Tub with hose threads | Y / N |  | ASSE 1011,1052 |
| Inside Hose Bibb(s) | Y / N |  | ASSE 1011,1052 |
| Toilet(s) | Y / N |  | ASSE 1002 |
| Boiler | Y / N |  | ASSE 1012** - Low Hazard ASSE 1013** - High Hazard |
| Humidifier | Y / N |  | ASME A112.1.2** ASSE 1012** |
| Outside Hose Bibb(s) | Y / N |  | ASSE 1019, 1053 ASSE 1011, 1052 |
| Lawn Irrigation | Y / N |  | ASSE 1001** ASSE 1020** ASSE 1013** |
| Hand Held showers | Y / N |  | ASSE 1014 ASME A112.18.1 |
| Water Powered Sump Pump |  |  | ASSE 1013** |
| Pools / Spa /Hot Tubs | Y / N |  | ASME A112.1.2 ** ASSE 1001** |
| Kitchen Faucets | Y /N |  | ASME A112.18.1 |
| Other |  |  |  |
| Other |  |  |  |
| Other |  |  |  |

Notes:______________________________________________________

Backflow Prevention Devices, Assemblies and methods must conform to the following National Standards as indicated in WI Dept of Safety & Professional Services Chapter Comm 82.41. State plumbing code and consultant information can be found online at: http://dsps.wi.gov/sb/SB-PlumbingProgram.html

- ASME A112.1.2	Air Gap - The unobstructed vertical distance between the lowest point of any pipe, faucet or fixture and the FLOOD LEVEL RIM of the receptor into which it is discharging.

- ASSE 1011*	Hose Bibb Vacuum Breaker (for indoor use)

- ASSE 1002*	Anti-Siphon Ball Cock for Gravity Water Closet  Flush Tanks

- ASSE 1012	Vented Dual Check Valve - For supplies to untreated boilers with less than 15 psig steam or maximum water pressure of 30 psig.

- ASSE 1019	Vacuum Breaker wall hydrants, freeze resistant automatic draining type

- ASSE 1011*	Anti–Frost Hose Bibb Vacuum Breaker - For use on outside hose bibbs where it could be exposed to freezing.

- ASSE 1013	Reduced Pressure Principle Backflow Prevention Assembly – Requires State registration and annual testing by a certified tester.

- ASSE 1014	Vacuum breaker for hand held showers

- ASSE 1001	Atmospheric Vacuum Breaker - Critical Level of AVB must be installed at least 6” above all downstream piping and No valves downstream.

- ASSE 1020	Pressure Vacuum Breaker - This assembly is not allowed for indoor installations. Requires State registration & annual testing by a certified tester.

- ASSE 1056 	Spill–Resistant Vacuum Breaker - Critical Level of SVB must be installed at least 6” above all downstream piping. Requires State registration & annual testing by a certified tester.

- ASME A112.1.3	Air-gap Fittings for use with plumbing fixtures and appliances

- ASME A112.18.1	Plumbing Supply Fittings

- ASSE 1053	Dual Check Backflow Preventer Wall Hydrant Freeze Resistant  Type

- ASSE 1052	Hose Connection Backflow Preventers

*These backflow preventers can be found at hardware stores. A local plumbing permit may be required for some installations.

**State Plumbing code may allow other devices under certain hydraulic/pumping/hazard conditions.

NOTICE:  Cross connections identified during the survey must be corrected within ____ days of the initial survey visit. When corrective action is completed, please call #_______________________to arrange for a follow up compliance verification survey by authorized personnel or with any questions you may have.

Customer Signature:________________________________________________Date:_________________________